## Sheet
wo_id | equipment_tag | date | type | failure_code | downtime_hrs | description | technician
WO-2023-0001 | HX-202A | 2023-08-01 | preventive |  | 3 | Scheduled backflush and performance reading per SOP-105. | J. Fernandes
WO-2023-0002 | P-103A | 2023-11-03 | inspection |  | 0 | Visual and NDE inspection completed per schedule. | K. Nair
WO-2023-0003 | P-101B | 2023-11-09 | corrective | ELP | 4.5 | Motor tripping on overload. Found loose terminal connection; remade and retested. | A. Sharma
WO-2023-0004 | P-101A | 2023-11-10 | preventive |  | 1.2 | Cleaned suction strainer per SOP-114 monthly schedule. | K. Nair
WO-2023-0005 | P-102A | 2023-11-15 | preventive |  | 0.6 | Alignment check and coupling inspection. | M. Patel
WO-2023-0006 | HX-201A | 2023-11-16 | preventive |  | 2.6 | Scheduled backflush and performance reading per SOP-105. | V. Reddy
WO-2023-0007 | P-101B | 2023-11-22 | preventive |  | 3 | Cleaned suction strainer per SOP-114 monthly schedule. | K. Nair
WO-2023-0008 | P-103A | 2023-12-19 | corrective | OHE | 9.4 | Approach temperature rising; unit fouled. Cleaned per SOP-105 and restored performance. | M. Patel
WO-2023-0009 | P-102B | 2023-12-28 | preventive |  | 1.1 | Alignment check and coupling inspection. | A. Sharma
WO-2023-0010 | HX-201B | 2023-12-28 | preventive |  | 0.6 | Gasket joint survey and thermal performance check. | V. Reddy
WO-2024-0011 | CV-302A | 2024-01-06 | inspection |  | 0 | Ultrasonic thickness survey at CMLs, readings within limits. | A. Sharma
WO-2024-0012 | CV-301A | 2024-01-11 | preventive |  | 2.3 | Packing gland inspection and air set filter service. | R. Kumar
WO-2024-0013 | CV-301A | 2024-01-11 | inspection |  | 0 | Visual and NDE inspection completed per schedule. | R. Kumar
WO-2024-0014 | P-101C | 2024-01-12 | preventive |  | 0.6 | Scheduled lubrication and vibration route reading per SOP-110. | R. Kumar
WO-2024-0015 | HX-201A | 2024-01-14 | corrective | LEK | 5.4 | Flange leak at discharge joint. Renewed gasket and retorqued to bolting table. | K. Nair
WO-2024-0016 | P-101B | 2024-01-17 | corrective | LEK | 7.7 | Casing drain plug weeping. Resealed plug and confirmed leak-free at operating pressure. | A. Sharma
WO-2024-0017 | P-101B | 2024-02-03 | inspection |  | 0 | Visual and NDE inspection completed per schedule. | A. Sharma
WO-2024-0018 | P-102B | 2024-03-02 | corrective | OHE | 12.2 | Approach temperature rising; unit fouled. Cleaned per SOP-105 and restored performance. | A. Sharma
WO-2024-0019 | P-102B | 2024-03-05 | inspection |  | 0 | Visual and NDE inspection completed per schedule. | M. Patel
WO-2024-0020 | P-102B | 2024-03-18 | corrective | VIB | 10.5 | High vibration reported on route reading, zone C. Balanced impeller and corrected coupling alignment. | M. Patel
WO-2024-0021 | CV-302A | 2024-03-24 | inspection |  | 0 | Ultrasonic thickness survey at CMLs, readings within limits. | M. Patel
WO-2024-0022 | P-101A | 2024-03-30 | preventive |  | 1.4 | Cleaned suction strainer per SOP-114 monthly schedule. | V. Reddy
WO-2024-0023 | P-101B | 2024-04-13 | preventive |  | 1.2 | Cleaned suction strainer per SOP-114 monthly schedule. | V. Reddy
WO-2024-0024 | P-101C | 2024-04-17 | corrective | SER | 5.8 | Mechanical seal leaking at drive end. Replaced seal cartridge per SOP-103 and flushed seal pot. | D. Singh
WO-2024-0025 | P-102B | 2024-04-19 | corrective | SER | 4.4 | Mechanical seal leaking at drive end. Replaced seal cartridge per SOP-103 and flushed seal pot. | S. Iyer
WO-2024-0026 | P-102A | 2024-04-21 | preventive |  | 2.5 | Scheduled lubrication and vibration route reading per SOP-110. | M. Patel
WO-2024-0027 | HX-201A | 2024-04-22 | preventive |  | 1.9 | Gasket joint survey and thermal performance check. | J. Fernandes
WO-2024-0028 | P-103A | 2024-06-11 | preventive |  | 2.1 | Alignment check and coupling inspection. | M. Patel
WO-2024-0029 | P-101A | 2024-06-19 | corrective | VIB | 8.4 | High vibration reported on route reading, zone C. Balanced impeller and corrected coupling alignment. | R. Kumar
WO-2024-0030 | P-103A | 2024-06-22 | corrective | SER | 5.5 | Seal weep worsened to steady drip. Fitted new cartridge seal, corrected seal chamber run-out. | S. Iyer
WO-2024-0031 | HX-202A | 2024-07-01 | corrective | VIB | 11 | High vibration reported on route reading, zone C. Balanced impeller and corrected coupling alignment. | R. Kumar
WO-2024-0032 | CV-303A | 2024-07-04 | preventive |  | 2.1 | Stroke test and positioner check per SOP-108. | D. Singh
WO-2024-0033 | HX-202A | 2024-07-12 | preventive |  | 2.9 | Gasket joint survey and thermal performance check. | S. Iyer
WO-2024-0034 | CV-302A | 2024-07-13 | preventive |  | 1.2 | Stroke test and positioner check per SOP-108. | D. Singh
WO-2024-0035 | HX-201B | 2024-07-21 | preventive |  | 1.7 | Gasket joint survey and thermal performance check. | K. Nair
WO-2024-0036 | P-102B | 2024-08-06 | preventive |  | 1.6 | Scheduled lubrication and vibration route reading per SOP-110. | S. Iyer
WO-2024-0037 | CV-302A | 2024-08-13 | corrective | ELP | 2.3 | Motor tripping on overload. Found loose terminal connection; remade and retested. | A. Sharma
WO-2024-0038 | P-102A | 2024-08-18 | inspection |  | 0 | Ultrasonic thickness survey at CMLs, readings within limits. | S. Iyer
WO-2024-0039 | P-101A | 2024-08-23 | preventive |  | 2.6 | Scheduled lubrication and vibration route reading per SOP-110. | D. Singh
WO-2024-0040 | CV-301A | 2024-09-01 | preventive |  | 2.4 | Stroke test and positioner check per SOP-108. | A. Sharma
WO-2024-0041 | P-101C | 2024-09-02 | preventive |  | 0.7 | Scheduled lubrication and vibration route reading per SOP-110. | K. Nair
WO-2024-0042 | P-101B | 2024-09-04 | preventive |  | 2.5 | Cleaned suction strainer per SOP-114 monthly schedule. | V. Reddy
WO-2024-0043 | P-102A | 2024-09-23 | corrective | SER | 5.6 | Seal weep worsened to steady drip. Fitted new cartridge seal, corrected seal chamber run-out. | D. Singh
WO-2024-0044 | P-102A | 2024-09-23 | preventive |  | 0.6 | Scheduled lubrication and vibration route reading per SOP-110. | A. Sharma
WO-2024-0045 | P-101B | 2024-09-23 | inspection |  | 0 | Routine thermography survey completed, no anomaly. | A. Sharma
WO-2024-0046 | CV-302A | 2024-09-24 | inspection |  | 0 | Routine thermography survey completed, no anomaly. | R. Kumar
WO-2024-0047 | HX-201A | 2024-09-26 | preventive |  | 2.5 | Gasket joint survey and thermal performance check. | J. Fernandes
WO-2025-0048 | P-101A | 2025-01-25 | preventive |  | 1.3 | Alignment check and coupling inspection. | V. Reddy
WO-2025-0049 | P-101B | 2025-01-30 | preventive |  | 0.9 | Alignment check and coupling inspection. | V. Reddy
WO-2025-0050 | P-102A | 2025-02-20 | corrective | LEK | 3.4 | Flange leak at discharge joint. Renewed gasket and retorqued to bolting table. | V. Reddy
WO-2025-0051 | HX-201A | 2025-02-21 | preventive |  | 1.6 | Gasket joint survey and thermal performance check. | V. Reddy
WO-2025-0052 | HX-201A | 2025-02-27 | inspection |  | 0 | Routine thermography survey completed, no anomaly. | S. Iyer
WO-2025-0053 | P-102A | 2025-03-02 | preventive |  | 3 | Scheduled lubrication and vibration route reading per SOP-110. | J. Fernandes
WO-2025-0054 | P-102B | 2025-03-03 | preventive |  | 0.9 | Alignment check and coupling inspection. | K. Nair
WO-2025-0055 | HX-201B | 2025-03-03 | preventive |  | 1.8 | Scheduled backflush and performance reading per SOP-105. | D. Singh
WO-2025-0056 | P-101C | 2025-03-09 | corrective | PLU | 2.8 | Tripped on low suction pressure. Suction strainer found heavily plugged; cleaned element per SOP-114. | M. Patel
WO-2025-0057 | CV-301A | 2025-04-05 | preventive |  | 1.9 | Packing gland inspection and air set filter service. | K. Nair
WO-2025-0058 | P-101C | 2025-04-07 | preventive |  | 1.7 | Scheduled lubrication and vibration route reading per SOP-110. | S. Iyer
WO-2025-0059 | CV-303A | 2025-04-15 | inspection |  | 0 | Ultrasonic thickness survey at CMLs, readings within limits. | J. Fernandes
WO-2025-0060 | CV-302A | 2025-04-29 | corrective | LEK | 4.6 | Casing drain plug weeping. Resealed plug and confirmed leak-free at operating pressure. | R. Kumar
WO-2025-0061 | HX-202A | 2025-05-04 | inspection |  | 0 | Ultrasonic thickness survey at CMLs, readings within limits. | K. Nair
WO-2025-0062 | P-101A | 2025-05-06 | corrective | BRG | 21.9 | DE bearing failed with audible rumble. Replaced both bearings, cleaned housing, renewed oil. | V. Reddy
WO-2025-0063 | HX-202A | 2025-05-07 | corrective | ELP | 2.9 | Motor tripping on overload. Found loose terminal connection; remade and retested. | K. Nair
WO-2025-0064 | P-102A | 2025-05-10 | corrective | OHE | 11.1 | High bearing housing temperature. Restored cooling water flow and flushed cooler lines. | V. Reddy
WO-2025-0065 | HX-202A | 2025-05-13 | corrective | BRG | 39.3 | Bearing seizure on start. Replaced bearing set, checked shaft journal, realigned driver. | S. Iyer
WO-2025-0066 | P-101C | 2025-05-27 | corrective | LEK | 5.6 | Flange leak at discharge joint. Renewed gasket and retorqued to bolting table. | R. Kumar
WO-2025-0067 | P-103A | 2025-05-29 | preventive |  | 2.5 | Scheduled lubrication and vibration route reading per SOP-110. | A. Sharma
WO-2025-0068 | CV-303A | 2025-06-18 | preventive |  | 1.2 | Packing gland inspection and air set filter service. | D. Singh
WO-2025-0069 | P-101B | 2025-06-22 | preventive |  | 1.6 | Alignment check and coupling inspection. | S. Iyer
WO-2025-0070 | P-101A | 2025-06-25 | preventive |  | 1.4 | Cleaned suction strainer per SOP-114 monthly schedule. | J. Fernandes
WO-2025-0071 | P-102A | 2025-07-01 | corrective | BRG | 30.7 | DE bearing failed with audible rumble. Replaced both bearings, cleaned housing, renewed oil. | J. Fernandes
WO-2025-0072 | P-102A | 2025-07-02 | inspection |  | 0 | Routine thermography survey completed, no anomaly. | R. Kumar
WO-2025-0073 | CV-302A | 2025-07-03 | preventive |  | 1.9 | Packing gland inspection and air set filter service. | A. Sharma
WO-2025-0074 | HX-202A | 2025-07-06 | preventive |  | 2.6 | Gasket joint survey and thermal performance check. | A. Sharma
WO-2025-0075 | HX-201A | 2025-07-30 | preventive |  | 1.5 | Scheduled backflush and performance reading per SOP-105. | A. Sharma
WO-2025-0076 | P-102B | 2025-08-06 | corrective | LKE | 4.9 | Casing drain plug weeping. Resealed plug and confirmed leak-free at operating pressure. | A. Sharma
WO-2025-0077 | P-102A | 2025-08-11 | preventive |  | 1.9 | Scheduled lubrication and vibration route reading per SOP-110. | J. Fernandes
WO-2025-0078 | P-101A | 2025-08-18 | corrective | SER | 4.9 | Mechanical seal leaking at drive end. Replaced seal cartridge per SOP-103 and flushed seal pot. | K. Nair
WO-2025-0079 | P-102A | 2025-08-26 | corrective | VIB | 9.1 | Repeat high vibration on DE bearing, zone C on route. Realigned and returned to service; root cause not established. | D. Singh
WO-2025-0080 | P-101B | 2025-08-28 | inspection |  | 0 | Visual and NDE inspection completed per schedule. | J. Fernandes
WO-2025-0081 | HX-201B | 2025-09-05 | corrective | BRG | 17.2 | DE bearing failed with audible rumble. Replaced both bearings, cleaned housing, renewed oil. | D. Singh
WO-2025-0082 | P-101B | 2025-09-25 | corrective | PLU | 2.9 | Low discharge flow. Strainer element choked with debris; cleaned and refitted per SOP-114. | D. Singh
WO-2025-0083 | HX-202A | 2025-09-29 | corrective | OHE | 15.8 | High bearing housing temperature. Restored cooling water flow and flushed cooler lines. | V. Reddy
WO-2025-0084 | CV-303A | 2025-10-03 | inspection |  | 0 | Visual and NDE inspection completed per schedule. | V. Reddy
WO-2025-0085 | P-102B | 2025-10-07 | preventive |  | 2.8 | Cleaned suction strainer per SOP-114 monthly schedule. | J. Fernandes
WO-2025-0086 | HX-201B | 2025-10-12 | preventive |  | 2.1 | Gasket joint survey and thermal performance check. | M. Patel
WO-2025-0087 | CV-301A | 2025-11-07 | preventive |  | 0.9 | Stroke test and positioner check per SOP-108. | D. Singh
WO-2025-0088 | P-101C | 2025-11-09 | preventive |  | 1.1 | Cleaned suction strainer per SOP-114 monthly schedule. | M. Patel
WO-2025-0089 | CV-301A | 2025-11-13 | inspection |  | 0 | Ultrasonic thickness survey at CMLs, readings within limits. | D. Singh
WO-2025-0090 | P-101A | 2025-11-14 | corrective | SER | 4.5 | Seal weep worsened to steady drip. Fitted new cartridge seal, corrected seal chamber run-out. | R. Kumar
WO-2025-0091 | P-101B | 2025-11-25 | preventive |  | 2.2 | Cleaned suction strainer per SOP-114 monthly schedule. | J. Fernandes
WO-2025-0092 | P-101A | 2025-11-30 | preventive |  | 1.2 | Cleaned suction strainer per SOP-114 monthly schedule. | K. Nair
WO-2025-0093 | HX-201A | 2025-12-02 | corrective | BRG | 25.8 | Bearing seizure on start. Replaced bearing set, checked shaft journal, realigned driver. | K. Nair
WO-2025-0094 | P-102A | 2025-12-04 | corrective | VIB | 10.6 | Repeat high vibration on DE bearing, zone C on route. Realigned and returned to service; root cause not established. | V. Reddy
WO-2025-0095 | HX-201A | 2025-12-18 | preventive |  | 2.4 | Scheduled backflush and performance reading per SOP-105. | J. Fernandes
WO-2025-0096 | CV-301A | 2025-12-20 | corrective | BRG | 18.6 | Bearing seizure on start. Replaced bearing set, checked shaft journal, realigned driver. | A. Sharma
WO-2025-0097 | HX-201B | 2025-12-25 | corrective | ELP | 2.1 | Intermittent trip on start. Megger test on motor windings passed; replaced faulty contactor. | J. Fernandes
WO-2025-0098 | P-103A | 2025-12-30 | corrective | VIB | 6.6 | High vibration reported on route reading, zone C. Balanced impeller and corrected coupling alignment. | R. Kumar
WO-2026-0099 | P-102A | 2026-01-22 | preventive |  | 1.6 | Cleaned suction strainer per SOP-114 monthly schedule. | V. Reddy
WO-2026-0100 | CV-303A | 2026-01-28 | corrective | ELP | 2.8 | Motor tripping on overload. Found loose terminal connection; remade and retested. | D. Singh
WO-2026-0101 | P-101A | 2026-02-06 | corrective | SER | 4.3 | Mechanical seal leaking at drive end. Replaced seal cartridge per SOP-103 and flushed seal pot. | M. Patel
WO-2026-0102 | P-102A | 2026-03-24 | corrective | VIB | 6.5 | Repeat high vibration on DE bearing, zone C on route. Realigned and returned to service; root cause not established. | M. Patel
WO-2026-0103 | P-101A | 2026-05-03 | corrective | SER | 7.2 | Seal weep worsened to steady drip. Fitted new cartridge seal, corrected seal chamber run-out. | M. Patel
WO-2026-0104 | P-101A | 2026-05-04 | preventive |  | 2.8 | Alignment check and coupling inspection. | M. Patel
WO-2026-0105 | P-101B | 2026-05-05 | preventive |  | 2.2 | Cleaned suction strainer per SOP-114 monthly schedule. | J. Fernandes
WO-2026-0106 | P-102B | 2026-05-16 | preventive |  | 1.4 | Alignment check and coupling inspection. | S. Iyer
WO-2026-0107 | P-103A | 2026-05-16 | preventive |  | 1 | Scheduled lubrication and vibration route reading per SOP-110. | R. Kumar
WO-2026-0108 | HX-201B | 2026-05-20 | preventive |  | 2.9 | Scheduled backflush and performance reading per SOP-105. | V. Reddy
WO-2026-0109 | P-101B | 2026-05-25 | inspection |  | 0 | Routine thermography survey completed, no anomaly. | D. Singh
WO-2026-0110 | HX-201A | 2026-05-31 | preventive |  | 1.7 | Scheduled backflush and performance reading per SOP-105. | A. Sharma
WO-2026-0111 | HX-202A | 2026-06-08 | preventive |  | 2.2 | Scheduled backflush and performance reading per SOP-105. | R. Kumar
WO-2026-0112 | P-101C | 2026-06-09 | preventive |  | 1.1 | Scheduled lubrication and vibration route reading per SOP-110. | D. Singh
WO-2026-0113 | P-101A | 2026-06-11 | inspection |  | 0 | Visual and NDE inspection completed per schedule. | R. Kumar
WO-2026-0114 | CV-303A | 2026-06-14 | preventive |  | 2 | Packing gland inspection and air set filter service. | D. Singh
WO-2026-0115 | CV-302A | 2026-06-18 | preventive |  | 1.8 | Packing gland inspection and air set filter service. | J. Fernandes
WO-2026-0116 | P-102A | 2026-06-20 | preventive |  | 2.2 | Scheduled lubrication and vibration route reading per SOP-110. | S. Iyer
WO-2026-0117 | P-101A | 2026-06-22 | corrective | PLU | 2.8 | Tripped on low suction pressure. Suction strainer found heavily plugged with monsoon debris; cleaned element per SOP-114. | R. Kumar
WO-2026-0118 | CV-301A | 2026-06-26 | preventive |  | 2.9 | Stroke test and positioner check per SOP-108. | D. Singh
WO-2026-0119 | P-102A | 2026-07-02 | corrective | VIB | 11.4 | Repeat high vibration on DE bearing, zone C on route. Realigned and returned to service; root cause not established. | K. Nair